## Instructions
Version:1.7 |  | Installation Area infromation |  | Select for the material list

Read the Area classification
information and decide what
item of equipment JB3 is.

Select an item from the
dropdown list by clicking on
the item. Eg JB 3
If you select the correct item
the selection box will turn green.
If you select incorrectly the selection
box will stay the same colour.

Once you have chosen the item. |  | 
Next choose a gland. |  | Once you have chosen the gland. | One by one select all items of accessories
|  | Next choose a Blanking element | Choosing required or not required or
|  | If it is not required select Not Required | choose an appropriate accessory.
Once you have completed your choices all the selection boxes should be green.
Note: In some cases there is more than one correct choice.

## Guide
IP Washers: | Only select IP washers to meet the requirements of the hazardous area and the type of protection for the equipment.
In general, Where the enclosure threaded entry is less than 6mm thick or where the equipment has an unthreaded (clearance) hole.
Lock nuts: | Select where enclosure has an unthreaded (clearance) holes or where the enclosure threaded entry is less than 6mm thickness.
If you select a serrated washer you will need to fit a lock nut to secure it in place.
Serrated Washer: | Select where a metal enclosure is supplied with an armoured cable which has threaded entry is less than 6mm thick
or where the equipment has an unthreaded (clearance) holes.
Select where a non-conducting enclosure is supplied with an armoured cable which has an internal earth plate.
Earth Tab/Tag: | Select where a non-conducting enclosure is supplied with an armoured cable which has NO internal earth plate.

## JB 1
Material list
Junction_Box
|  |  | Number-Material-Certification |  | IP | Entries
|  |  | 1 Metal II 2G Ex d IIB T6 Gb |  | IP65 | 4 x 20mm 10mm Thread
|  |  | 2 Metal |  | IP55 | 4 x 20mm 8mm Thread
|  |  | 3 Steel II 2G Ex e II T4 |  | IP54 | 1 x 20mm Clearance
|  |  | 4 Metal II 2G Ex ec II T6 Gc |  |  | 2 x 20mm Clearance
|  |  | 5 Plastic |  | IP66 | 3 x 20mm Clearance
|  |  | 6 Plastic Ex eb IIC T4 Gb |  | IP66 | 3 x 20mm 5mm Thread, No Internal Earth Plate
|  |  | 7 Plastic II 2G Ex e II T6 Gb |  | IP66 | 3 x 20mm 6mm Thread, Internal Earth Plate
|  |  | 8 Plastic II 3G Ex nA II T6 |  | IP66 | 4 x 20mm 3mm Thread, Internal Earth Plate
|  |  | 9 Metal II 2G Ex db IIC T5 Gb |  | IP66 | 3 x 20mm 10mm Thread
Accessories Note: Various numbers of accessories are available to use.
|  |  | Gland |  | Blank_Elements
|  |  | Gland E1W Metal II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Metal II 2G Ex d IIC
|  |  | Gland E1W Metal Barrier II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Plastic II 2G Ex e IIC
|  |  | Gland E1W Metal |  | Blank 20mm Plastic
|  |  | Gland A2 Metal II 2G Ex d IIC Ex e IIC 20mm |  | Blank Cert NPT Metal II 2G Ex d IIC
|  |  | Gland A2 Metal 20mm |  | Not Required
|  |  | Gland A2 Plastic 20mm |  | Earth Tag
|  |  | Gland A2 Metal II 2G Ex d IIC NPT |  | Required
Not Required
JB 1 | IP Washer | Thread Adaptor
|  |  | IP Washer | Adaptor | Lock Nut |  | Serrated Washer
Gland 1 | Lock Nut | Serrated Washer | Sealing + Metal Washer (nR) | Cert Adaptor Metal II 2G Ex d IIC | Required |  | Required
|  |  | Required | Required | Not Required |  | Not Required
Blanking Element |  | Earth Tag | Not Required | Not Required
ZZT 2021
Choose the minimum requirement for accessories

## LT 1
Material list
Light
|  |  | Number-Material-Certification |  | IP | Entries
|  |  | 1 Metal II 2G Ex d IIB T6 Gb |  | IP54 | 2 x 20mm Clearance
|  |  | 2 Plastic II 2G Ex e IIC T6 Gb |  | IP54 | 2 x 20mm 8mm Thread
|  |  | 3 Steel II 3G Ex nR II T6 Gc |  | IP66 | 2 x 20mm 10mm Thread
|  |  | 4 Plastic II 2G Ex eb IIC T6 Gb |  | IP66 | 3 x 20mm 5mm Thread, Internal Earth Plate
Accessories Note: Various numbers of accessories are available to use.
|  |  | Gland |  | Blank_Elements
|  |  | Gland E1W Metal II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Metal II 2G Ex d IIC
|  |  | Gland E1W Metal Barrier II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Plastic II 2G Ex e IIC
|  |  | Gland E1W Metal |  | Blank 20mm Plastic
|  |  | Gland A2 Metal II 2G Ex d IIC Ex e IIC 20mm |  | Blank Cert NPT Metal II 2G Ex d IIC
|  |  | Gland A2 Metal 20mm |  | Not Required
|  |  | Gland A2 Plastic 20mm |  | Earth Tag
|  |  | Gland A2 Metal II 2G Ex d IIC NPT |  | Required
Not Required
Light | IP Washer | Thread Adaptor
|  |  | IP Washer | Adaptor | Lock Nut |  | Serrated Washer
Gland 1 | Lock Nut | Serrated Washer | Sealing + Metal Washer (nR) | Cert Adaptor Metal II 2G Ex d IIC | Required |  | Required
|  |  | Required | Required | Not Required |  | Not Required
Blanking Element |  | Earth Tag | Not Required | Not Required
ZZT 2021
Choose the minimum requirement for accessories

## JB 3
Material list
Junction_Box
|  |  | Number-Material-Certification |  | IP | Entries
|  |  | 1 Metal II 2G Ex d IIB T6 Gb |  | IP66 | 2 x 20mm 10mm Thread
|  |  | 2 Plastic Ex eb IIC T4 Gb |  | IP66 | 3 x 20mm 5mm Thread, No Internal Earth Plate
|  |  | 3 Plastic II 2G Ex e II T6 Gb |  | IP54 | 3 x 20mm 6mm Thread, Internal Earth Plate
|  |  | 4 Plastic II 3G Ex nA II T6 |  | IP66 | 4 x 20mm 3mm Thread, Internal Earth Plate
|  |  | 5 Metal II 2G Ex db IIC T5 Gb |  | IP66 | 3 x 20mm 10mm Thread
Accessories Note: Various numbers of accessories are available to use.
|  |  | Gland |  | Blank_Elements
|  |  | Gland E1W Metal II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Metal II 2G Ex d IIC
|  |  | Gland E1W Metal Barrier II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Plastic II 2G Ex e IIC
|  |  | Gland E1W Metal |  | Blank 20mm Plastic
|  |  | Gland A2 Metal II 2G Ex d IIC Ex e IIC 20mm |  | Blank Cert NPT Metal II 2G Ex d IIC
|  |  | Gland A2 Metal 20mm |  | Not Required
|  |  | Gland A2 Plastic 20mm |  | Earth Tag
|  |  | Gland A2 Metal II 2G Ex d IIC NPT |  | Required
Not Required
JB 3 | IP Washer | Thread Adaptor
|  |  | IP Washer | Adaptor | Lock Nut |  | Serrated Washer
Gland 1 | Lock Nut | Serrated Washer | Sealing + Metal Washer (nR) | Cert Adaptor Metal II 2G Ex d IIC | Required |  | Required
|  |  | Required | Required | Not Required |  | Not Required
Gland 2 | Blanking Element | Earth Tag | Not Required | Not Required
ZZT 2021
Choose the minimum requirement for accessories

## IS JB 1
Material list
Junction_Box
|  |  | Number-Material-Certification |  | IP | Entries
|  |  | 1 Metal II 2G Ex d IIB T6 Gb |  | IP65 | 4 x 20mm 10mm Thread
|  |  | 2 Metal |  | IP55 | 4 x 20mm 8mm Thread
|  |  | 3 Plastic Ex eb IIC T4 Gb |  | IP66 | 3 x 20mm 5mm Thread, No Internal Earth Plate
|  |  | 4 Plastic II 2G Ex ia IIC T6 Gb |  | IP66 | 3 x 20mm 6mm Thread, Internal Earth Plate
|  |  | 5 Metal II 2G Ex db IIC T5 Gb |  | IP66 | 2 x 20mm 10mm Thread
Accessories Note: Various numbers of accessories are available to use.
|  |  | Gland |  | Blank_Elements
|  |  | Gland E1W Metal II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Metal II 2G Ex d IIC
|  |  | Gland E1W Metal Barrier II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Plastic II 2G Ex e IIC
|  |  | Gland E1W Metal |  | Blank 20mm Plastic
|  |  | Gland A2 Metal II 2G Ex d IIC Ex e IIC 20mm |  | Blank Cert NPT Metal II 2G Ex d IIC
|  |  | Gland A2 Metal 20mm |  | Not Required
|  |  | Gland A2 Plastic 20mm |  | Earth Tag
|  |  | Gland A2 Metal II 2G Ex d IIC NPT |  | Required
Not Required
JB 1 | IP Washer | Thread Adaptor
|  |  | IP Washer | Adaptor | Lock Nut |  | Serrated Washer
Gland 1 | Lock Nut | Serrated Washer | Sealing + Metal Washer (nR) | Cert Adaptor Metal II 2G Ex d IIC | Required |  | Required
|  |  | Required | Required | Not Required |  | Not Required
Blanking Element |  | Earth Tag | Not Required | Not Required
ZZT 2021
Choose the minimum requirement for accessories

## IS Sensor 1
Material list
Sensors
|  |  | Number-Material-Certification |  | IP | Entries
|  |  | 1 Metal II 2G Ex ib IIC T6 Gb |  | IP65 | 2 x NPT Thread
|  |  | 2 Metal |  | IP55 | 2 x 20mm Clearance
|  |  | 3 Plastic II 1G Ex ia IIB T4 Ga |  | IP54 | 2 x 20mm 5mm Threaded
|  |  | 4 Metal II 1G Ex ia IIC T6 Ga |  | IP66 | 2 x 20mm 8mm Threaded
|  |  | 5 Plastic |  | IP66 | 3 x 20mm Clearance
|  |  | 6 Plastic II 1G Ex ia IIC T6 Ga |  | IP54 | 2 x 20mm 8mm Threaded
|  |  | 7 Plastic II 2G Ex ib IIC T6 Gb |  | IP66 | 2 x 20mm 5mm Threaded
|  |  | 8 Plastic II 1G Ex ia IIC T4 Ga |  | IP66 | 1 x NPT Threaded
Accessories Note: Various numbers of accessories are available to use.
|  |  | Gland |  | Blank_Elements
|  |  | Gland E1W Metal II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Metal II 2G Ex d IIC
|  |  | Gland E1W Metal Barrier II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Plastic II 2G Ex e IIC
|  |  | Gland E1W Metal |  | Blank 20mm Plastic
|  |  | Gland A2 Metal II 2G Ex d IIC Ex e IIC 20mm |  | Blank Cert NPT Metal II 2G Ex d IIC
|  |  | Gland A2 Metal 20mm |  | Not Required
|  |  | Gland A2 Plastic 20mm |  | Earth Tag
|  |  | Gland A2 Metal II 2G Ex d IIC NPT |  | Required
Not Required
JB 1 | IP Washer | Thread Adaptor
|  |  | IP Washer | Adaptor | Lock Nut |  | Serrated Washer
Gland 1 | Lock Nut | Serrated Washer | Sealing + Metal Washer (nR) | Cert Adaptor Metal II 2G Ex d IIC | Required |  | Required
|  |  | Required | Required | Not Required |  | Not Required
Blanking Element |  | Earth Tag | Not Required | Not Required
ZZT 2021
Choose the minimum requirement for accessories

## IS Sensor 2
Material list
Sensors
|  |  | Number-Material-Certification |  | IP | Entries
|  |  | 1 Metal II 2G Ex ib IIC T6 Gb |  | IP65 | 2 x NPT Thread
|  |  | 2 Metal |  | IP55 | 2 x 20mm Clearance
|  |  | 3 Plastic II 1G Ex ia IIB T4 Ga |  | IP54 | 2 x 20mm 5mm Threaded
|  |  | 4 Metal II 1G Ex ia IIC T6 Ga |  | IP66 | 2 x 20mm 8mm Threaded
|  |  | 5 Plastic |  | IP66 | 3 x 20mm Clearance
|  |  | 6 Plastic II 1G Ex ia IIC T6 Ga |  | IP54 | 2 x 20mm 8mm Threaded
|  |  | 7 Plastic II 2G Ex ib IIC T6 Gb |  | IP66 | 2 x 20mm 5mm Threaded
|  |  | 8 Plastic II 1G Ex ia IIC T4 Ga |  | IP66 | 1 x NPT Threaded
Accessories Note: Various numbers of accessories are available to use.
|  |  | Gland |  | Blank_Elements
|  |  | Gland E1W Metal II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Metal II 2G Ex d IIC
|  |  | Gland E1W Metal Barrier II 2G Ex d IIC Ex e IIC |  | Blank Cert 20mm Plastic II 2G Ex e IIC
|  |  | Gland E1W Metal |  | Blank 20mm Plastic
|  |  | Gland A2 Metal II 2G Ex d IIC Ex e IIC 20mm |  | Blank Cert NPT Metal II 2G Ex d IIC
|  |  | Gland A2 Metal 20mm |  | Not Required
|  |  | Gland A2 Plastic 20mm |  | Earth Tag
|  |  | Gland A2 Metal II 2G Ex d IIC NPT |  | Required
Fit equipment to achieve the MINIMUM requirements. |  |  |  |  | Not Required
JB 1 | IP Washer | Thread Adaptor
|  |  | IP Washer | Adaptor | Lock Nut |  | Serrated Washer
Gland 1 | Lock Nut | Serrated Washer | Sealing + Metal Washer (nR) | Cert Adaptor Metal II 2G Ex d IIC | Required |  | Required
|  |  | Required | Required | Not Required |  | Not Required
Blanking Element |  | Earth Tag | Not Required | Not Required
ZZT 2021
Choose the minimum requirement for accessories